JSC “NPG Granit-Salamandra”

Generator of extinguishing aerosol AGS-8

PASSPORT

INFORMATION ON THE PRODUCT:

Generator AGS-8/1	AGS -8/2		batch No_______________

Aerosol forming compound			batch No _______________

Date of manufacturing				_______________________

MAIN TECHNICAL CHARACTERISTICS:

Semi-hermetic protected volume	AGS-8/1	60 m3

AGS-8/2	124 m3

Mass of aerosol forming compound	AGS-8/1	3.25 kg

AGS-8/2	6.7 kg

Warranty period – 18 months, including 12 months of storage.

Operating life – 5 years, including 1 year of the storage

Lifetime – 10 years

After expiration of the operating period the question of its prolongation can be solved by the Manufacturer.

COMPLETENESS OF THE PACKAGE:

Generator AGS-8

Instruction Manual

Bracket

Generator is completed with the starter in accordance with the order.

Generator conforms to Technical Conditions 4854-081-54876390-01

The packing conforms to the requirements of engineering documentation

Department of technical control

Address:

JSC :NPG Granit-Salamandra”

Izhorskaya str., 13/19 125412 Moscow

Tel: 485-8454, 485-9827

JSC “NPG Granit-Salamandra”

INSTRUCTION MANUAL

For the extinguishing aerosol generators

of operational use

AGS-8

RE 4854-081-54876390-2003

Moscow, 2014

- APPLICATION

Generator of extinguishing aerosol ags-8 (hereinafter – generator) is the mean of volume fire extinguishing is designed for localization and suppression of fires of solid combustible materials (wood, insulating materials, plastics etc.), inflammable liquids (petrol, oil refinery products, organic solvents, etc.), electrical insulating materials and electrical live equipment with voltage up to 40 kV.

Generators are not applied for extinguishing of alkaline metals, as well as for extinguishing of substances which are burning without air access.

Generators should be used in accordance with the valid norms (SP 5.13130.2009 “Automatic fire alarm and fire extinguishing systems”)

Generators are produced in two modifications:

AGS-8/1 with mass of aerosol compound 3.25 kg

AGS-8/2 with mass of aerosol compound 6.7 kg

- DESIGN OF GENERATOR AGS-8

Generator (see the drawing) consists of the body (1) inside which an aerosol forming compound (2) is located, the starter (3) and the injector (4).   Aerosol forming compound is separated from the shell of the body by the heat insulating material (5).  There are nozzle holes (6) in the cover of the body through which the aerosol comes out, and the threaded sleeve for binding of the starter. Generator is installed in the protected room with the special bracket (7), which is supplied with the generator. There is a jack (8) on the bracket for connecting of the electrical starter and the starting device.

AGS-8/1:

AGS-8/2:

- PRINCIPAL OF OPERATION

The principal of generator operation is based on the inhibiting of oxidation-reduction reactions by the highly dispersed product (aerosol) of alkali metals salts and oxides which can stay suspended for a long period. Aerosol is produced in the process of burning of the solid aerosol forming compound which is located inside the generator shell.

After generator starts its operation concentration of the oxygen in the protected room remain almost the same.

The settled aerosol can be removed from the different surfaces with the wet cloth or vacuum cleaner.

- TECHNICAL CHARACTERISTICS OF GENERATOR AGS-8

Mass of generator:

AGS-8/1				10.0 + 1.5 kg

AGS-8/2				18.0 + 2.0 kg

Mass of aerosol forming compound:

AGS-8/1				3.25 + 0.1 kg

AGS-8/2				6.7 + 0.2 kg

Aerosol extinguishing ability			0.054 kg/m3

Maximum volume of protected semi-hermetic room (δ  < 0.001 m-1*):

AGS-8/1				60 m3

AGS-8/2				124 m3

*) δ – is ratio of the total area of the openings to the volume of protected room

Operating period:

AGS-8/1				78 +/- 11 sec

AGS-8/2				140 +/- 21 sec

Dimensions (with injector, without bracket):

- Diameter				220 mm

- Length		AGS-8/1		220 mm

AGS-8/2		50 mm

Operating conditions:

- Temperature				from – 50 °C to + 50 °C

- Relative humidity			up to 98%

- Mechanical effect 0.5 g in the frequency band up to 35 Hz

Heat quantity which is distinguished during generator operation:

AGS-8/1		12000 kJ

AGS-8/2		25500 kJ

Lifetime after installation			5 years

For generator activation the special starters are used: electrical and thermochemical. The use of thermochemical starters which activate when the temperature in the protected volume reaches 150 – 170 ⁰C, allows each generator to operate autonomously. The use of electrical starters allows to use generators as part of automatic aerosol fire extinguishing systems.

Electrical starters have the following characteristics:

- Minimum starting current – 0.4A

- Type of current – direct (DC) or alternating (AC)

- Duration of impulse – not less than 0.5 sec

- Resistance of electrical initiator of the starter – 2.5 – 4.5 Om

Maximum current of control of generator starting chain should not exceed:

- At constant control – 0.005 A

- At periodical control during no more than 2 minutes with breaks not less than 10 minutes – 0.05A.

The starter type should be chosen by the Buyer.

- DEFINING OF THE NECESSARY QUANTITY OF GENERATORS AGS-8 AND THEIR ALLOCATION IN THE PROTECTED ROOM

  - The design and installation work on aerosol fire extinguishing systems should be fulfilled by the specialized organizations which have the license for such type of service.

  - Calculation of generator quantity necessary for protection of the given room is made according to the methodology contained in the valid norms.

  - Generators should be installed in such way to provide quick and even filling of the protected room with the aerosol. For this purpose:

    - Generators should be located evenly at the whole area of the room;

    - If necessary generators should be located in groups (no more than 12 units for AGS-8/1 and no more than 6 units for AGS-8/2);

    - The distance between generators axis in the group should be not less than 0.5 m;

    - The distance between groups of generators should not exceed 20 m.

  - The location of generator and the direction of nozzles should be chosen that way to provide the most free spreading of the aerosol flow which enters from the injector.

  - Generators should be located in the protected rooms according the following requirements:

    - The axis of aerosol flow should not be directed towards the people located at a distance less than 2 meters;

    - The distance from generator to the fence or wall should be not less than 50 mm;

    - The distance from generator to the equipment, stored materials, property, electrical appliances should be not less than 300 mm;

    - No walls, fencing, equipment, materials should be located in the space limited by radius of 0.2 m from generator axis and length of 1.5 meters from the injector in direction of aerosol flow entrance;

    - Generators can not be installed on the burning basement;

    - There should be an access to installed generator for control and prevention works.

  - If several generators are used for protection of one space, their simultaneous activation should be provided.

  - If generators with electrical starter are used, the forced switch off of ventilation before generators activation should be provided.

  - For reducing of starting period of generator with thermochemical starter, it is recommended to install in the protected room with heat sensitive cord which should be allocated in the upper part of the room and in the places of most possible ignition. The cord should be connected to the heat sensitive element of the starter.

  - If several generators are installed in one room, thermochemical starters should be connected between each other with the heat sensitive cord.  This provides simultaneous staring of generators.

- PREPARATION OF GENERATOR FOR OPERATION AND ITS ACTIVATION

  - Generators are anchored of the room walls with the attached bracket (7).

  - After generator is mounted and the whole installation of the fire extinguishing system is finished, the starter (3) is screwed into the threaded sleeve carefully.

  - During installation of thermochemical starter it is necessary to keep heat sensitive cord undamaged.

.

- ACCIDENT PREVENTION DURING INSTALLATION AND OPERATION

  - During work with generators and starters it should be considered that they contain the inflammable compositions

  - During installation of electrical starters the endings of cables should be shorted. Their connection to the jack on injector should be done after commissioning of the whole automatic fire extinguishing system.

  - Electrical equipment of premises in which generators with electrical starters are installed should conform to requirements of Electric systems operation.

  - At the design of generator electrical starting chains there should be provided the measures which exclude the appearance of current pickup which can lead to the accidental start of generators.

  - When fire starts and generators are activated, people located in the premises should leave it rapidly, close the doors and call fire brigade.

  - In is not recommended to use generators in the premises which can not be abandoned before generators start their operation.

  - If it is impossible to leave the room quickly, the respiratory should be protected from the impact of the aerosol particles with the fabric bandage or gauze.

  - It should be kept in mind that during generator operation the temperature on the injector can reach 400 ⁰C, and in front of it there is a zone with diameter of 0.1 m where the temperature reaches 200 ⁰C at a distance of 0.25 m and 75 ⁰C at a distance of 1.5 m.

IT IS FORBIDDEN:

- To use generators for manual extinguishing of fire;

- To make the welding at a distance less than 2 meters from generator;

- To use damaged generators;

- Dismantle the generator.

- To try to prevent the following activation of generator after the rope noose of the starter is pulled out.

- MARKING, PACKING, STORAGE AND TRANSPORTATION OF GENERATORS AGS-8

  - There are serial numbers of aerosol forming compound, generator, manufacturing date, mass of compound and maximum protected volume in the passport and on the label of generator.

  - Generators AGS-8 are supplied by the Manufacturer packed into the pasteboard boxes.

  - Generators and starters in Manufacturer’s packing can be transported by all means of transportation.

  - Generators should be stored in the Manufacturer packing in the closed storage rooms under the temperature from +5°C to +40°C and relative humidity up to 80% without the presence of aggressive environment.

  - Storage life of generators is up to 5 years.

  - Generators can be stored in a pile, but no higher than 2 stages one on another (according to the Manufacturer packing)

Some changes of generator construction which will not influence on its operating ability can be made.